## 英文封面
Revision：4.3
Product Specification
| Product Model: |  |  | High Temperature Nickel-Cadmium Battery
| Product Type: |  |  | ESP3000CHT
| Draw up： |  | Technical Department
| Date： | 24/11/2010
ESP reserves the right to alter or amend the design,model and specification without prior notice.

## 英文1
Document Title：Product Specification of |  |  |  | Ni-Cd | ESP3000CHT |  |  | Revision：4.3
１、 SCOPE
This specification governs the performance of the following Nickel-Cadmium
cylindrical cell and its stack-up battery.
| Model： | ESP3000CHT
| Cell Size： | Ccrew cut(25.2±0.1×49.0±0.5) mm
Ccusp(25.2±0.2×49.5±0.5) mm
2 、DATA OF STACK UP BATTERIES
All data involve voltage and weight of stack-up batteries are equal to the value of unit cell
multiplied by the number of unit cell which consisted in the stack-up batteries.
Example ：Stack-up batteries consisting three unit cells
Nominal voltage of unit cell=1.2V
Nominal voltage of stack-up batteries =1.2V×3=3.6V
3、 RATINGS
| Description |  | Unit | Specification |  |  | Condition
| Nominal Voltage |  | V/cell | 1.2 |  |  | Unit cell or stack-up batteries
| Nominal Capacity |  | mAh | 3000 |  |  | Standard Charge/Discharge
| Standard Charge |  | mA |  | 300 | (0.1C) | Ta=20±5℃
|  |  | hour | 14~16
| Trickle Charge |  | mA | (0.03C)~(0.05C) |  |  | Ta=0~70℃
| Standard discharge |  | mA |  | 600 | (0.2C) | Ta= 20±5℃ Humidity：Max85%
| Discharge Cut-off Voltage |  | V/cell | 1
| Storage Temperature |  | ℃ | -20~30(Within 1 year)* |  |  | Discharged state Humidity：Max85%
-20~40(Within 6 months)
-20~50(Within 1 month)
-20~60(Within 1 week)
| Typical Weight |  | Gram | 74 |  |  | unit cell
*To keep the best performance for those not used for a long time,we recommend to charge and
discharge the cells/batteries at least once in every 6 months.
4、 PERFORMANCE
Unless otherwise stated, tests should be done within one month of delivery under the
following conditions：
ESP reserves the right to alter or amend the design,model and specification without prior notice.

## 英文2
Document Title：Product Specification of |  |  |  |  | Ni-Cd | ESP3000CHT |  |  | Revision：4.3
Ambient Temperature ：20±5℃
Relative Humidity ： 65±20%
Notes： Standard Charge/Discharge conditions：
| Charge： |  | 300 | mA(0.1C)× 14 hours
| Discharge： |  | 600 | mA(0.2C) to 1.0V/cell
Test |  | Unit | Specification |  | Condition |  |  |  | Remarks
Capacity |  | mAh | ≥ | 3000 | Standard Charge/Discharge |  |  |  | up to 3 cycles are allowed
Open Circuit Voltage(OCV) |  | V | ≥ | 1.25 | Within l hour after standard charge
Internal Impedance |  | mΩ | ≤ | 12 | Upon fully charged(lKHz)
High Rate Discharge(1C) |  | min | ≥ | 48 | Standard Charge, l hour rest before discharge by 1C to 1.0V/cell |  |  |  | up to 3 cycles are allowed
Charge Retention |  | mAh | ≥ | 1950 | Standard Charge, Storage 28days， Standard Discharge |  |  |  | Ta=20℃±5℃
Permanent Charge Endurance Test |  | min | T1,T2≥ | 225 | IEC61951-1(2003)7.4.2.3 |  |  |  | See Table 1
|  | min | T3,T4≥ | 150
Charge acceptance |  |  |  |  | Cycle No. | Charge | Rest | Discharge | See Note 1
[5 empty] | 1 | 0.05C×48h | None | 0.2C to 1.0V/cell
|  | min | ≥ | 225 | 2 | 0.05C×24h | None | 0.2C to 1.0V/cell
|  | min | ≥ | 225 | 3 | 0.05C×24h | None | 0.2C to 1.0V/cell
IEC Cycle Life |  | Cycle | ≥ | 500 | IEC61951-1(2003)7.4.1.1 |  |  |  | See Table 2
Leakage |  |  | No leakage nor deformation |  | Fully charged at : |  | 150 | mA for 28 days
at 0±2℃.
Vibration Resistance |  | N/A | Change of voltage should be less than 0.02V/cell,change of impedance should be less than 5milliohm/cell |  | Charge the battery at 0.1C for 14hrs,then leave for 24hrs,check battery before/after vibration,amplitude 1.5mm,vibration 3000 CPM,any direction for 60mins.
Impact Resistance |  | N/A | Change of voltage should be less than 0.02V/cell,change of impedance should be less than 5milliohm/cell |  | Charge the battery at 0.1C for 14hrs,then leave for 24hrs,check battery before/after dropped,height 50 cm wooden board(thickness 30mm)direction not specified,3 times.
5、CONFIGURATION, DIMENSIONS AND MARKINGS
Please refer to the attached drawing.
ESP reserves the right to alter or amend the design,model and specification without prior notice.

## 英文3
Document Title：Product Specification of |  |  |  | Ni-Cd | ESP3000CHT |  | Revision：4.3
6、EXTERNAL APPEARANCE
The cell/battery shall be free from cracks, scars, breakage, rust, discoloration, leakage or deformation.
7、WARRANTY
One year limited warranty against workmanship and material defects.
8、CAUTION
[1]Reverse charging is not acceptable.
[2]Charge before use. The cells/batteries are delivered in an uncharged state. | [6 empty] | ESP
[3]Do not charge/discharge with more than our specified current.
[4]Do not short circuit the cell/battery permanent damage to the cells/batteries may result.
[5]Do not incinerate or mutilate the cells/batteries.
[6]Do not solder directly to the cells/batteries.
[7]The expected life may be reduced if the cells/batteries are subjected to adverse conditions as:
extreme temperature, deep cycling, excessive overcharge/ over-discharge.
[8]Store the cells/batteries in a cool dry place. Always discharge batteries before packing.
Table 1: | IEC61951-1(2003)7.4.2.3 Permanent Charge Endurance Test:
| Cycle Number | Ambient temperature | Charge |  | Rest | Discharge | Discharge capacity
| 1 | +40℃±2℃ | 0.05C×48h |  | None | 0.2C to 1.0V/cell
| 2 |  | 0.05C×24h |  | None | 0.2C to 1.0V/cell | T1
| 3 |  | 0.05C×24h |  | None | 0.2C to 1.0V/cell | T2
| 4 | +70℃±2℃ | 0.05C×60d |  | None | 0.2C to 1.0V/cell
| 5 |  | 0.05C×60d |  | None | 0.2C to 1.0V/cell
| 6 |  | 0.05C×60d |  | None | 0.2C to 1.0V/cell
| 7 | +40℃±2℃ | 0.05C×48h |  | None | 0.2C to 1.0V/cell
| 8 |  | 0.05C×24h |  | None | 0.2C to 1.0V/cell | T3
| 9 |  | 0.05C×24h |  | None | 0.2C to 1.0V/cell | T4
Table 2: | IEC61951-1(2003)7.4.1.1 Cycle Life:
| Cycle No. | Charge |  | Rest | Discharge
| 1 | 0.1C×16h |  | None | 0.25C×2h20min
| 2-48 | 0.25C×3h10min |  | None | 0.25C×2h20min
| 49 | 0.25C×3h10min |  | None | 0.25C to 1.0V/cell
| 50 | 0.1C×16h |  | 1-4h | 0.2C to 1.0V/cell
Cycle l to 50 shall be repeated until the discharge duration on any 50th cycle becomes less than 3 h.
Notes: (1)Before test,the cell shall be discharged at 0.2C to 1.0V/cell ,and stored 16h～24h at 55℃±2℃.
(2)Ta: Ambient Temperature.
ESP reserves the right to alter or amend the design,model and specification without prior notice.

## 英文图
JJJ Battery Co.,LTD.
MODEL No: |  | ESP3000CHT |  | Description: |  | 3000 | mAh SIZE | Ni-Cd | C
Specification
[5 empty] | Nominal Capacity |  |  | 3000 | mAh
[5 empty] | Nominal Voltage |  |  | 1.2 | V
[5 empty] | Charge current |  | Trickle | 150 | mA
[7 empty] | Standard | 300 | mA
[5 empty] | Charge time |  | Trickle | 48 | Hrs~
[7 empty] | Standard | 14~16 | Hrs
[5 empty] | Ambient Temperature | Charge | Trickle | 0℃~70℃
[7 empty] | Standard | 0℃~70℃
Dimensions(without Tube) (mm) | [5 empty] | Discharge |  | -20℃~70℃
D | 25.20±0.10 |  |  |  |  | Storage |  | -20℃~60℃
d1 | 8.50±0.08 | d2 | 6.00±0.08 |  | Internal Impedance(mΩ) (After Charge) |  |  | ≤ | 12
H1 | 49.00±0.50 | H2 | 49.50±0.50
h1 | 48.50±0.50 | h2 | 47.50±0.50 |  | Weight |  |  | 74 | g
ESP reserves the right to alter or amend the design,model and specification without prior notice.